## 50 HP
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.5 | 45 | -7°C | 10%*Note 3 | 35°C | 3.11 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C | 2.41 | 45 | -7°C |  | 55°C*Note 4 | 2.14 | 15
2°C |  | 35°C | 3.98 | 150 |  | 2°C |  | 35°C | 4.37 | 90 | 2°C |  | 35°C | 4.34 | 45 | 2°C |  | 35°C | 4 | 15
2°C |  | 45°C | 3.26 | 150 |  | 2°C |  | 45°C | 3.47 | 90 | 2°C |  | 45°C | 3.35 | 45 | 2°C |  | 45°C | 3.2 | 15
2°C |  | 55°C | 2.76 | 136 |  | 2°C |  | 55°C | 2.82 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 150 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.88 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 5.15 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the EER (Energy Efficiency Ratio) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.4 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.47 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 8.75 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 4.99 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.55 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 35% | 12/ 10.6/ 14 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 151 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30%*Note 2 | 35°C | 3.59 | 54 | -7°C | 10%*Note 3 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.95 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C | 2.52 | 54 | -7°C |  | 55°C*Note 4 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.42 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 157 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 4.97 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3.87 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 169 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.84 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.45 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.39 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the EER (Energy Efficiency Ratio) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 | 180 |  | 20°C | 60% | 7°C | 7.26 | 108 | 20°C | 30%*Note 1 | 7°C | 7.59 | 54 | 20°C | 10%*Note 2 | 7°C | 6.39 | 18
20°C |  | 12°C | 7.79 | 180 |  | 20°C |  | 12°C | 9.5 | 108 | 20°C |  | 12°C | 10.5 | 54 | 20°C |  | 12°C | 8.25 | 18
20°C |  | 18°C | 8.41 | 180 |  | 20°C |  | 18°C | 11 | 108 | 20°C |  | 18°C | 14 | 54 | 20°C |  | 18°C | 12.1 | 18
25°C |  | 7°C | 4.85 | 180 |  | 25°C |  | 7°C | 5.86 | 108 | 25°C |  | 7°C | 8.91 | 54 | 25°C |  | 7°C | 5.24 | 18
25°C |  | 12°C | 6.13 | 180 |  | 25°C |  | 12°C | 7.34 | 108 | 25°C |  | 12°C | 8.11 | 54 | 25°C |  | 12°C | 6.55 | 18
25°C |  | 18°C | 6.67 | 180 |  | 25°C |  | 18°C | 8.63 | 108 | 25°C |  | 18°C | 11.4 | 54 | 25°C |  | 18°C | 9.29 | 18
30°C |  | 7°C | 3.96 | 180 |  | 30°C |  | 7°C | 4.76 | 108 | 30°C |  | 7°C | 4.88 | 54 | 30°C |  | 7°C | 6.56 | 18
30°C |  | 12°C | 4.91 | 180 |  | 30°C |  | 12°C | 5.8 | 108 | 30°C |  | 12°C | 6.27 | 54 | 30°C |  | 12°C | 5.27 | 18
30°C |  | 18°C | 5.41 | 180 |  | 30°C |  | 18°C | 6.97 | 108 | 30°C |  | 18°C | 8.41 | 54 | 30°C |  | 18°C | 7.1 | 18
35°C |  | 7°C | 3.26 | 180 |  | 35°C |  | 7°C | 3.9 | 108 | 35°C |  | 7°C | 3.99 | 54 | 35°C |  | 7°C | 3.66 | 18
35°C |  | 12°C | 3.99 | 180 |  | 35°C |  | 12°C | 4.67 | 108 | 35°C |  | 12°C | 4.93 | 54 | 35°C |  | 12°C | 4.31 | 18
35°C |  | 18°C | 4.46 | 180 |  | 35°C |  | 18°C | 5.67 | 108 | 35°C |  | 18°C | 6.8 | 54 | 35°C |  | 18°C | 5.54 | 18
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 161L/Min

## 70 HP
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.01 | 190 |  | -7°C | 60% | 35°C | 3.42 | 120 | -7°C | 30%*Note 2 | 35°C | 3.61 | 60 | -7°C | 10%*Note 3 | 35°C | 3.31 | 20
-7°C |  | 45°C | 2.59 | 185 |  | -7°C |  | 45°C | 2.86 | 120 | -7°C |  | 45°C | 2.94 | 60 | -7°C |  | 45°C | 2.68 | 20
-7°C |  | 55°C*Note 1 | 2.36 | 167 |  | -7°C |  | 55°C*Note 1 | 2.47 | 120 | -7°C |  | 55°C*Note 1 | 2.53 | 60 | -7°C |  | 55°C*Note 4 | 2.3 | 20
2°C |  | 35°C | 3.65 | 200 |  | 2°C |  | 35°C | 4.3 | 120 | 2°C |  | 35°C | 4.45 | 60 | 2°C |  | 35°C | 4.05 | 20
2°C |  | 45°C | 3.08 | 200 |  | 2°C |  | 45°C | 3.45 | 120 | 2°C |  | 45°C | 3.52 | 60 | 2°C |  | 45°C | 3.16 | 20
2°C |  | 55°C | 2.65 | 185 |  | 2°C |  | 55°C | 2.83 | 120 | 2°C |  | 55°C | 2.83 | 60 | 2°C |  | 55°C | 2.53 | 20
7°C |  | 35°C | 4.11 | 200 |  | 7°C |  | 35°C | 4.9 | 120 | 7°C |  | 35°C | 4.99 | 60 | 7°C |  | 35°C | 4.61 | 20
7°C |  | 45°C | 3.39 | 200 |  | 7°C |  | 45°C | 3.84 | 120 | 7°C |  | 45°C | 3.87 | 60 | 7°C |  | 45°C | 3.47 | 20
7°C |  | 55°C | 2.86 | 200 |  | 7°C |  | 55°C | 3.1 | 120 | 7°C |  | 55°C | 3.06 | 60 | 7°C |  | 55°C | 2.7 | 20
12°C |  | 35°C | 4.81 | 200 |  | 12°C |  | 35°C | 5.64 | 120 | 12°C |  | 35°C | 5.93 | 60 | 12°C |  | 35°C | 5.26 | 20
12°C |  | 45°C | 3.84 | 200 |  | 12°C |  | 45°C | 4.33 | 120 | 12°C |  | 45°C | 4.39 | 60 | 12°C |  | 45°C | 3.98 | 20
12°C |  | 55°C | 3.18 | 200 |  | 12°C |  | 55°C | 3.45 | 120 | 12°C |  | 55°C | 3.45 | 60 | 12°C |  | 55°C | 3.05 | 20
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 179L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 5.64 | 200 |  | 20°C | 60% | 7°C | 7.15 | 120 | 20°C | 30%*Note 1 | 7°C | 7.73 | 60 | 20°C | 10%*Note 2 | 7°C | 6.91 | 20
20°C |  | 12°C | 7.35 | 200 |  | 20°C |  | 12°C | 9.29 | 120 | 20°C |  | 12°C | 10.1 | 60 | 20°C |  | 12°C | 8.27 | 20
20°C |  | 18°C | 7.97 | 200 |  | 20°C |  | 18°C | 10.5 | 120 | 20°C |  | 18°C | 12.8 | 60 | 20°C |  | 18°C | 11.4 | 20
25°C |  | 7°C | 4.56 | 200 |  | 25°C |  | 7°C | 5.76 | 120 | 25°C |  | 7°C | 6.18 | 60 | 25°C |  | 7°C | 5.67 | 20
25°C |  | 12°C | 5.8 | 200 |  | 25°C |  | 12°C | 7.2 | 120 | 25°C |  | 12°C | 7.83 | 60 | 25°C |  | 12°C | 6.57 | 20
25°C |  | 18°C | 6.37 | 200 |  | 25°C |  | 18°C | 8.27 | 120 | 25°C |  | 18°C | 12 | 60 | 25°C |  | 18°C | 9.2 | 20
30°C |  | 7°C | 3.73 | 200 |  | 30°C |  | 7°C | 4.69 | 120 | 30°C |  | 7°C | 4.99 | 60 | 30°C |  | 7°C | 4.57 | 20
30°C |  | 12°C | 4.68 | 200 |  | 30°C |  | 12°C | 5.71 | 120 | 30°C |  | 12°C | 6.11 | 60 | 30°C |  | 12°C | 5.3 | 20
30°C |  | 18°C | 5.2 | 200 |  | 30°C |  | 18°C | 6.62 | 120 | 30°C |  | 18°C | 8.8 | 60 | 30°C |  | 18°C | 7.04 | 20
35°C |  | 7°C | 3.08 | 200 |  | 35°C |  | 7°C | 3.84 | 120 | 35°C |  | 7°C | 4.08 | 60 | 35°C |  | 7°C | 3.7 | 20
35°C |  | 12°C | 3.81 | 200 |  | 35°C |  | 12°C | 4.6 | 120 | 35°C |  | 12°C | 4.85 | 60 | 35°C |  | 12°C | 4.33 | 20
35°C |  | 18°C | 4.31 | 200 |  | 35°C |  | 18°C | 5.36 | 120 | 35°C |  | 18°C | 6.58 | 60 | 35°C |  | 18°C | 5.52 | 20
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 56.6/66.9/70.8 | 3.11 | 2.63 | 2.36 | 176 | 176 | 167
2°C | 54% | 24.7/30.9/37.9 | 4.37 | 3.49 | 2.85 | 108 | 108 | 108
7°C | 35% | 13.9/17.9/22.7 | 5.03 | 3.9 | 3.09 | 70 | 70 | 70
12°C | 12% *Note2 | 4.33/5.88/7.62 | 5.54 | 4.08 | 3.15 | 24 | 24 | 24
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 52.9/41.7/38.9 | 3.33 | 4.22 | 4.53 | 176 | 176 | 176
30°C | 54% | 22.5/18.3/15.4 | 4.79 | 5.91 | 7.02 | 108 | 108 | 108
25°C | 35% | 11.5/8.34/5.83 | 6.08 | 8.39 | 12 | 70 | 70 | 70
20°C | 12%*Note 1 | 3.46/2.76/2.29 | 6.94 | 8.71 | 10.5 | 24 | 24 | 24
*Note 1 - Values provided based on minimum flow rate conditions of 179L/Min

## 50 HP Pump 1.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.5 | 45 | -7°C | 10%*Note 3 | 35°C | 3.11 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C | 2.41 | 45 | -7°C |  | 55°C | 2.14 | 15
2°C |  | 35°C | 3.97 | 150 |  | 2°C |  | 35°C | 4.35 | 90 | 2°C |  | 35°C | 4.32 | 45 | 2°C |  | 35°C | 3.98 | 15
2°C |  | 45°C | 3.25 | 150 |  | 2°C |  | 45°C | 3.46 | 90 | 2°C |  | 45°C | 3.44 | 45 | 2°C |  | 45°C | 2.93 | 15
2°C |  | 55°C | 2.74 | 136 |  | 2°C |  | 55°C | 2.81 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 150 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.88 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 5.15 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
2. Table of Cooling Performance (EER)
This table should show the EER (Energy Efficiency Ratio) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.4 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.47 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 8.75 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 4.99 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.55 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | COP 35℃ | COP 45℃ | COP 55°C | LWT 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 35% | 12/ 10.6/ 14 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP Pump 1.5kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 151 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30%*Note 2 | 35°C | 3.64 | 54 | -7°C | 10%*Note 3 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.95 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C*Note 1 | 2.52 | 54 | -7°C |  | 55°C*Note 4 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.48 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 151 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 5.02 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3.87 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 180 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.93 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.45 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.39 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 | 180 |  | 20°C | 60% | 7°C | 7.26 | 108 | 20°C | 30%*Note 1 | 7°C | 7.66 | 54 | 20°C | 10%*Note 2 | 7°C | 6.39 | 18
20°C |  | 12°C | 7.79 | 180 |  | 20°C |  | 12°C | 9.5 | 108 | 20°C |  | 12°C | 10.6 | 54 | 20°C |  | 12°C | 8.25 | 18
20°C |  | 18°C | 8.41 | 180 |  | 20°C |  | 18°C | 9.82 | 108 | 20°C |  | 18°C | 14 | 54 | 20°C |  | 18°C | 12.1 | 18
25°C |  | 7°C | 4.85 | 180 |  | 25°C |  | 7°C | 5.86 | 108 | 25°C |  | 7°C | 6.11 | 54 | 25°C |  | 7°C | 5.24 | 18
25°C |  | 12°C | 6.13 | 180 |  | 25°C |  | 12°C | 7.34 | 108 | 25°C |  | 12°C | 8.1 | 54 | 25°C |  | 12°C | 6.55 | 18
25°C |  | 18°C | 6.67 | 180 |  | 25°C |  | 18°C | 8.63 | 108 | 25°C |  | 18°C | 11.4 | 54 | 25°C |  | 18°C | 9.29 | 18
30°C |  | 7°C | 3.96 | 180 |  | 30°C |  | 7°C | 4.76 | 108 | 30°C |  | 7°C | 4.92 | 54 | 30°C |  | 7°C | 4.55 | 18
30°C |  | 12°C | 4.91 | 180 |  | 30°C |  | 12°C | 5.8 | 108 | 30°C |  | 12°C | 8.39 | 54 | 30°C |  | 12°C | 5.27 | 18
30°C |  | 18°C | 5.41 | 180 |  | 30°C |  | 18°C | 6.97 | 108 | 30°C |  | 18°C | 4.01 | 54 | 30°C |  | 18°C | 7.1 | 18
35°C |  | 7°C | 3.26 | 180 |  | 35°C |  | 7°C | 3.9 | 108 | 35°C |  | 7°C | 4.93 | 54 | 35°C |  | 7°C | 3.66 | 18
35°C |  | 12°C | 3.99 | 180 |  | 35°C |  | 12°C | 4.67 | 108 | 35°C |  | 12°C | 6.81 | 54 | 35°C |  | 12°C | 4.31 | 18
35°C |  | 18°C | 4.46 | 180 |  | 35°C |  | 18°C | 5.67 | 108 | 35°C |  | 18°C | 7.64 | 54 | 35°C |  | 18°C | 5.54 | 18
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% *Note2 | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 50 HP Pump 2.2kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.55 | 45 | -7°C | 10%*Note 3 | 35°C | 4.82 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C*Note 1 | 2.41 | 45 | -7°C |  | 55°C*Note 4 | 2.14 | 15
2°C |  | 35°C | 3.98 | 150 |  | 2°C |  | 35°C | 4.37 | 90 | 2°C |  | 35°C | 4.42 | 45 | 2°C |  | 35°C | 4 | 15
2°C |  | 45°C | 3.26 | 150 |  | 2°C |  | 45°C | 3.47 | 90 | 2°C |  | 45°C | 3.35 | 45 | 2°C |  | 45°C | 3.2 | 15
2°C |  | 55°C | 2.76 | 136 |  | 2°C |  | 55°C | 2.82 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 150 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.98 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 5.15 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.38 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.3 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 7.71 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 5.18 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.81 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | COP 35℃ | COP 45℃ | COP 55°C | LWT 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 35% | 12/ 10.6/ 14 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP Pump 2.2 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 151 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30%*Note 2 | 35°C | 3.64 | 54 | -7°C | 10%*Note 3 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.95 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C*Note 1 | 2.52 | 54 | -7°C |  | 55°C*Note 4 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.48 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 157 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 5.03 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3086 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 180 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.93 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.45 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.39 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 | 180 |  | 20°C | 60% | 7°C | 7.26 | 108 | 20°C | 30%*Note 1 | 7°C | 7.64 | 54 | 20°C | 10%*Note 2 | 7°C | 6.39 | 18
20°C |  | 12°C | 7.79 | 180 |  | 20°C |  | 12°C | 9.5 | 108 | 20°C |  | 12°C | 10.4 | 54 | 20°C |  | 12°C | 8.25 | 18
20°C |  | 18°C | 8.41 | 180 |  | 20°C |  | 18°C | 11 | 108 | 20°C |  | 18°C | 14 | 54 | 20°C |  | 18°C | 12.1 | 18
25°C |  | 7°C | 4.85 | 180 |  | 25°C |  | 7°C | 5.86 | 108 | 25°C |  | 7°C | 6.11 | 54 | 25°C |  | 7°C | 5.24 | 18
25°C |  | 12°C | 6.13 | 180 |  | 25°C |  | 12°C | 7.34 | 108 | 25°C |  | 12°C | 8.1 | 54 | 25°C |  | 12°C | 6.55 | 18
25°C |  | 18°C | 6.67 | 180 |  | 25°C |  | 18°C | 8.63 | 108 | 25°C |  | 18°C | 11.4 | 54 | 25°C |  | 18°C | 9.29 | 18
30°C |  | 7°C | 3.96 | 180 |  | 30°C |  | 7°C | 4.76 | 108 | 30°C |  | 7°C | 4.92 | 54 | 30°C |  | 7°C | 4.55 | 18
30°C |  | 12°C | 4.91 | 180 |  | 30°C |  | 12°C | 5.8 | 108 | 30°C |  | 12°C | 6.27 | 54 | 30°C |  | 12°C | 5.27 | 18
30°C |  | 18°C | 5.41 | 180 |  | 30°C |  | 18°C | 6.97 | 108 | 30°C |  | 18°C | 8.39 | 54 | 30°C |  | 18°C | 7.1 | 18
35°C |  | 7°C | 3.26 | 180 |  | 35°C |  | 7°C | 3.9 | 108 | 35°C |  | 7°C | 4.01 | 54 | 35°C |  | 7°C | 3.66 | 18
35°C |  | 12°C | 3.99 | 180 |  | 35°C |  | 12°C | 4.67 | 108 | 35°C |  | 12°C | 4.93 | 54 | 35°C |  | 12°C | 4.31 | 18
35°C |  | 18°C | 4.46 | 180 |  | 35°C |  | 18°C | 5.67 | 108 | 35°C |  | 18°C | 6.81 | 54 | 35°C |  | 18°C | 5.54 | 18
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% *Note2 | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 70 HP Pump 2.2 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.01 | 190 |  | -7°C | 60% | 35°C | 3.42 | 120 | -7°C | 30%*Note 2 | 35°C | 3.61 | 60 | -7°C | 10%*Note 3 | 35°C | 3.31 | 20
-7°C |  | 45°C | 2.59 | 185 |  | -7°C |  | 45°C | 2.86 | 120 | -7°C |  | 45°C | 2.94 | 60 | -7°C |  | 45°C | 2.68 | 20
-7°C |  | 55°C*Note 1 | 2.36 | 167 |  | -7°C |  | 55°C*Note 1 | 2.5 | 120 | -7°C |  | 55°C*Note 1 | 2.53 | 60 | -7°C |  | 55°C*Note 4 | 2.3 | 20
2°C |  | 35°C | 3.65 | 200 |  | 2°C |  | 35°C | 4.3 | 120 | 2°C |  | 35°C | 4.45 | 60 | 2°C |  | 35°C | 4.05 | 20
2°C |  | 45°C | 3.08 | 200 |  | 2°C |  | 45°C | 3.45 | 120 | 2°C |  | 45°C | 3.52 | 60 | 2°C |  | 45°C | 3.16 | 20
2°C |  | 55°C | 2.72 | 193 |  | 2°C |  | 55°C | 2.83 | 120 | 2°C |  | 55°C | 2.83 | 60 | 2°C |  | 55°C | 2.53 | 20
7°C |  | 35°C | 4.11 | 200 |  | 7°C |  | 35°C | 4.9 | 120 | 7°C |  | 35°C | 4.99 | 60 | 7°C |  | 35°C | 4.61 | 20
7°C |  | 45°C | 3.39 | 200 |  | 7°C |  | 45°C | 3.84 | 120 | 7°C |  | 45°C | 3.87 | 60 | 7°C |  | 45°C | 3.47 | 20
7°C |  | 55°C | 2.96 | 200 |  | 7°C |  | 55°C | 3.1 | 120 | 7°C |  | 55°C | 3.06 | 60 | 7°C |  | 55°C | 2.7 | 20
12°C |  | 35°C | 4.81 | 200 |  | 12°C |  | 35°C | 5.64 | 120 | 12°C |  | 35°C | 5.93 | 60 | 12°C |  | 35°C | 5.26 | 20
12°C |  | 45°C | 3.84 | 200 |  | 12°C |  | 45°C | 4.33 | 120 | 12°C |  | 45°C | 4.39 | 60 | 12°C |  | 45°C | 3.98 | 20
12°C |  | 55°C | 3.18 | 200 |  | 12°C |  | 55°C | 3.45 | 120 | 12°C |  | 55°C | 3.4 | 60 | 12°C |  | 55°C | 3.05 | 20
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 179L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 5.64 | 200 |  | 20°C | 60% | 7°C | 7.15 | 120 | 20°C | 30%*Note 1 | 7°C | 7.73 | 60 | 20°C | 10%*Note 2 | 7°C | 6.88 | 20
20°C |  | 12°C | 7.35 | 200 |  | 20°C |  | 12°C | 9.29 | 120 | 20°C |  | 12°C | 10.1 | 60 | 20°C |  | 12°C | 8.26 | 20
20°C |  | 18°C | 7.97 | 200 |  | 20°C |  | 18°C | 10.5 | 120 | 20°C |  | 18°C | 12.8 | 60 | 20°C |  | 18°C | 11.4 | 20
25°C |  | 7°C | 4.56 | 200 |  | 25°C |  | 7°C | 5.76 | 120 | 25°C |  | 7°C | 6.18 | 60 | 25°C |  | 7°C | 5.64 | 20
25°C |  | 12°C | 5.8 | 200 |  | 25°C |  | 12°C | 7.2 | 120 | 25°C |  | 12°C | 7.83 | 60 | 25°C |  | 12°C | 6.57 | 20
25°C |  | 18°C | 6.37 | 200 |  | 25°C |  | 18°C | 8.27 | 120 | 25°C |  | 18°C | 12 | 60 | 25°C |  | 18°C | 9.19 | 20
30°C |  | 7°C | 3.73 | 200 |  | 30°C |  |  | 4.69 | 120 | 30°C |  | 7°C | 4.99 | 60 | 30°C |  | 7°C | 4.54 | 20
30°C |  | 12°C | 4.68 | 200 |  | 30°C |  | 12°C | 5.71 | 120 | 30°C |  | 12°C | 6.11 | 60 | 30°C |  | 12°C | 5.3 | 20
30°C |  | 18°C | 5.2 | 200 |  | 30°C |  | 18°C | 6.62 | 120 | 30°C |  | 18°C | 8.8 | 60 | 30°C |  | 18°C | 7.03 | 20
35°C |  | 7°C | 3.08 | 200 |  | 35°C |  | 7°C | 3.84 | 120 | 35°C |  | 7°C | 4.08 | 60 | 35°C |  | 7°C | 3.68 | 20
35°C |  | 12°C | 3.81 | 200 |  | 35°C |  | 12°C | 4.6 | 120 | 35°C |  | 12°C | 4.85 | 60 | 35°C |  | 12°C | 4.63 | 20
35°C |  | 18°C | 4.31 | 200 |  | 35°C |  | 18°C | 5.36 | 120 | 35°C |  | 18°C | 6.58 | 60 | 35°C |  | 18°C | 5.52 | 20
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 179L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 56.6/66.9/70.8 | 3.11 | 2.63 | 2.36 | 176 | 176 | 167
2°C | 54% | 24.7/30.9/37.9 | 4.37 | 3.49 | 2.85 | 108 | 108 | 108
7°C | 35% | 13.9/17.9/22.7 | 5.03 | 3.9 | 3.09 | 70 | 70 | 70
12°C | 12% *Note2 | 4.33/5.88/7.62 | 5.54 | 4.08 | 3.15 | 24 | 24 | 24
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 52.9/41.7/38.9 | 3.33 | 4.22 | 4.53 | 176 | 176 | 176
30°C | 54% | 22.5/18.3/15.4 | 4.79 | 5.91 | 7.02 | 108 | 108 | 108
25°C | 35% | 11.5/8.34/5.83 | 6.08 | 8.39 | 12 | 70 | 70 | 70
20°C | 12%*Note 1 | 3.46/2.76/2.29 | 6.94 | 8.71 | 10.5 | 24 | 24 | 24
*Note 1 - Values provided based on minimum flow rate conditions of 179L/Min

## 50 HP Pump 3.7 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.5 | 45 | -7°C | 10%*Note 3 | 35°C | 3.11 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C*Note 1 | 2.41 | 45 | -7°C |  | 55°C*Note 4 | 2.14 | 15
2°C |  | 35°C | 3.98 | 150 |  | 2°C |  | 35°C | 4.37 | 90 | 2°C |  | 35°C | 4.34 | 45 | 2°C |  | 35°C | 4 | 15
2°C |  | 45°C | 3.26 | 150 |  | 2°C |  | 45°C | 3.47 | 90 | 2°C |  | 45°C | 3.53 | 45 | 2°C |  | 45°C | 3.2 | 15
2°C |  | 55°C | 2.76 | 136 |  | 2°C |  | 55°C | 2.82 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 150 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.88 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 5.15 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.4 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.47 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 8.75 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 4.99 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.55 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | COP 35℃ | COP 45℃ | COP 55°C | LWT 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | -7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 7°C | 35% | 10.6/ 14/ 17.47 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP Pump 3.7 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 151 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30%*Note 2 | 35°C | 3.64 | 54 | -7°C | 10%*Note 3 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.94 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C*Note 1 | 2.52 | 54 | -7°C |  | 55°C*Note 4 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.48 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 157 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 5.03 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3.86 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 169 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.93 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.44 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.47 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 | 180 |  | 20°C | 60% | 7°C | 7.26 | 108 | 20°C | 30%*Note 1 | 7°C | 7.66 | 54 | 20°C | 10%*Note 2 | 7°C | 6.39 | 18
20°C |  | 12°C | 7.79 | 180 |  | 20°C |  | 12°C | 11.4 | 108 | 20°C |  | 12°C | 10.6 | 54 | 20°C |  | 12°C | 8.25 | 18
20°C |  | 18°C | 8.41 | 180 |  | 20°C |  | 18°C | 11 | 108 | 20°C |  | 18°C | 14 | 54 | 20°C |  | 18°C | 12.1 | 18
25°C |  | 7°C | 4.85 | 180 |  | 25°C |  | 7°C | 5.86 | 108 | 25°C |  | 7°C | 6.09 | 54 | 25°C |  | 7°C | 5.24 | 18
25°C |  | 12°C | 6.13 | 180 |  | 25°C |  | 12°C | 7.34 | 108 | 25°C |  | 12°C | 8.16 | 54 | 25°C |  | 12°C | 6.55 | 18
25°C |  | 18°C | 6.67 | 180 |  | 25°C |  | 18°C | 8.63 | 108 | 25°C |  | 18°C | 11.5 | 54 | 25°C |  | 18°C | 9.29 | 18
30°C |  | 7°C | 3.96 | 180 |  | 30°C |  | 7°C | 4.76 | 108 | 30°C |  | 7°C | 4.91 | 54 | 30°C |  | 7°C | 4.55 | 18
30°C |  | 12°C | 4.91 | 180 |  | 30°C |  | 12°C | 5.8 | 108 | 30°C |  | 12°C | 6.31 | 54 | 30°C |  | 12°C | 5.27 | 18
30°C |  | 18°C | 5.41 | 180 |  | 30°C |  | 18°C | 6.97 | 108 | 30°C |  | 18°C | 8.45 | 54 | 30°C |  | 18°C | 7.1 | 18
35°C |  | 7°C | 3.26 | 180 |  | 35°C |  | 7°C | 3.9 | 108 | 35°C |  | 7°C | 4 | 54 | 35°C |  | 7°C | 3.66 | 18
35°C |  | 12°C | 3.99 | 180 |  | 35°C |  | 12°C | 4.67 | 108 | 35°C |  | 12°C | 4.96 | 54 | 35°C |  | 12°C | 4.31 | 18
35°C |  | 18°C | 4.46 | 180 |  | 35°C |  | 18°C | 5.67 | 108 | 35°C |  | 18°C | 6.85 | 54 | 35°C |  | 18°C | 5.54 | 18
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% *Note2 | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 70 HP Pump 3.7 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 301 | 190 |  | -7°C | 60% | 35°C | 3.42 | 120 | -7°C | 30%*Note 2 | 35°C | 3.61 | 60 | -7°C | 10%*Note 3 | 35°C | 3.31 | 20
-7°C |  | 45°C | 2.59 | 185 |  | -7°C |  | 45°C | 2.86 | 120 | -7°C |  | 45°C | 2.93 | 60 | -7°C |  | 45°C | 2.68 | 20
-7°C |  | 55°C*Note 1 | 2.36 | 167 |  | -7°C |  | 55°C*Note 1 | 2.5 | 120 | -7°C |  | 55°C*Note 1 | 2.52 | 60 | -7°C |  | 55°C*Note 4 | 2.3 | 20
2°C |  | 35°C | 3.65 | 200 |  | 2°C |  | 35°C | 4.3 | 120 | 2°C |  | 35°C | 4.45 | 60 | 2°C |  | 35°C | 4.05 | 20
2°C |  | 45°C | 3.08 | 200 |  | 2°C |  | 45°C | 3.45 | 120 | 2°C |  | 45°C | 3.5 | 60 | 2°C |  | 45°C | 3.16 | 20
2°C |  | 55°C | 2.72 | 193 |  | 2°C |  | 55°C | 2.83 | 120 | 2°C |  | 55°C | 2.82 | 60 | 2°C |  | 55°C | 2.53 | 20
7°C |  | 35°C | 4.11 | 200 |  | 7°C |  | 35°C | 4.9 | 120 | 7°C |  | 35°C | 4.99 | 60 | 7°C |  | 35°C | 4.61 | 20
7°C |  | 45°C | 3.39 | 200 |  | 7°C |  | 45°C | 3.84 | 120 | 7°C |  | 45°C | 3.85 | 60 | 7°C |  | 45°C | 3.47 | 20
7°C |  | 55°C | 2.86 | 200 |  | 7°C |  | 55°C | 3.1 | 120 | 7°C |  | 55°C | 3.04 | 60 | 7°C |  | 55°C | 2.7 | 20
12°C |  | 35°C | 4.81 | 200 |  | 12°C |  | 35°C | 5.64 | 120 | 12°C |  | 35°C | 5.93 | 60 | 12°C |  | 35°C | 5.26 | 20
12°C |  | 45°C | 3.84 | 200 |  | 12°C |  | 45°C | 4.33 | 120 | 12°C |  | 45°C | 4.37 | 60 | 12°C |  | 45°C | 3.98 | 20
12°C |  | 55°C | 3.18 | 200 |  | 12°C |  | 55°C | 3.45 | 120 | 12°C |  | 55°C | 3.38 | 60 | 12°C |  | 55°C | 3.05 | 20
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 179L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 5.64 | 200 |  | 20°C | 60% | 7°C | 7.15 | 120 | 20°C | 30%*Note 1 | 7°C | 7.64 | 60 | 20°C | 10%*Note 2 | 7°C | 6.88 | 20
20°C |  | 12°C | 7.35 | 200 |  | 20°C |  | 12°C | 9.29 | 120 | 20°C |  | 12°C | 10.4 | 60 | 20°C |  | 12°C | 8.26 | 20
20°C |  | 18°C | 7.97 | 200 |  | 20°C |  | 18°C | 10.5 | 120 | 20°C |  | 18°C | 12.8 | 60 | 20°C |  | 18°C | 11.4 | 20
25°C |  | 7°C | 4.56 | 200 |  | 25°C |  | 7°C | 5.76 | 120 | 25°C |  | 7°C | 6.11 | 60 | 25°C |  | 7°C | 5.64 | 20
25°C |  | 12°C | 5.8 | 200 |  | 25°C |  | 12°C | 7.2 | 120 | 25°C |  | 12°C | 8.08 | 60 | 25°C |  | 12°C | 6.57 | 20
25°C |  | 18°C | 6.37 | 200 |  | 25°C |  | 18°C | 8.27 | 120 | 25°C |  | 18°C | 10.7 | 60 | 25°C |  | 18°C | 9.19 | 20
30°C |  | 7°C | 3.73 | 200 |  | 30°C |  | 7°C | 4.69 | 120 | 30°C |  | 7°C | 4.93 | 60 | 30°C |  | 7°C | 4.54 | 20
30°C |  | 12°C | 4.68 | 200 |  | 30°C |  | 12°C | 5.71 | 120 | 30°C |  | 12°C | 6.27 | 60 | 30°C |  | 12°C | 5.3 | 20
30°C |  | 18°C | 5.2 | 200 |  | 30°C |  | 18°C | 6.62 | 120 | 30°C |  | 18°C | 9.09 | 60 | 30°C |  | 18°C | 7.03 | 20
35°C |  | 7°C | 3.08 | 200 |  | 35°C |  | 7°C | 3.84 | 120 | 35°C |  | 7°C | 4.04 | 60 | 35°C |  | 7°C | 3.68 | 20
35°C |  | 12°C | 3.81 | 200 |  | 35°C |  | 12°C | 4.6 | 120 | 35°C |  | 12°C | 4.95 | 60 | 35°C |  | 12°C | 4.63 | 20
35°C |  | 18°C | 4.31 | 200 |  | 35°C |  | 18°C | 5.36 | 120 | 35°C |  | 18°C | 6.76 | 60 | 35°C |  | 18°C | 5.52 | 20
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 179L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 56.6/66.9/70.8 | 3.11 | 2.63 | 2.36 | 176 | 176 | 167
2°C | 54% | 24.7/30.9/37.9 | 4.37 | 3.49 | 2.85 | 108 | 108 | 108
7°C | 35% | 13.9/17.9/22.7 | 5.03 | 3.9 | 3.09 | 70 | 70 | 70
12°C | 12% *Note2 | 4.33/5.88/7.62 | 5.54 | 4.08 | 3.15 | 24 | 24 | 24
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 52.9/41.7/38.9 | 3.33 | 4.22 | 4.53 | 176 | 176 | 176
30°C | 54% | 22.5/18.3/15.4 | 4.79 | 5.91 | 7.02 | 108 | 108 | 108
25°C | 35% | 11.5/8.34/5.83 | 6.08 | 8.39 | 12 | 70 | 70 | 70
20°C | 12%*Note 1 | 3.46/2.76/2.29 | 6.94 | 8.71 | 10.5 | 24 | 24 | 24
*Note 1 - Values provided based on minimum flow rate conditions of 179L/Min

## 50 HP Pump 5.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.5 | 45 | -7°C | 10%*Note 3 | 35°C | 3.11 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C*Note 1 | 2.41 | 45 | -7°C |  | 55°C*Note 4 | 2.14 | 15
2°C |  | 35°C | 3.98 | 150 |  | 2°C |  | 35°C | 4.37 | 90 | 2°C |  | 35°C | 4.34 | 45 | 2°C |  | 35°C | 4 | 15
2°C |  | 45°C | 3.26 | 150 |  | 2°C |  | 45°C | 3.47 | 90 | 2°C |  | 45°C | 3.35 | 45 | 2°C |  | 45°C | 3.2 | 15
2°C |  | 55°C | 2.76 | 136 |  | 2°C |  | 55°C | 2.82 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 140 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.88 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 2.91 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.4 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.47 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 8.75 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 4.99 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.55 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | COP 35℃ | COP 45℃ | COP 55°C | LWT 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 35% | 12/ 10.6/ 14 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP Pump 5.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 151 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30%*Note 2 | 35°C | 3.64 | 54 | -7°C | 10%*Note 3 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.94 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C*Note 1 | 2.52 | 54 | -7°C |  | 55°C*Note 4 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.48 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 157 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 5.03 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3.86 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 164 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.93 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.44 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.47 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 | 180 |  | 20°C | 60% | 7°C | 7.26 | 108 | 20°C | 30%*Note 1 | 7°C | 7.64 | 54 | 20°C | 10%*Note 2 | 7°C | 6.39 | 18
20°C |  | 12°C | 7.79 | 180 |  | 20°C |  | 12°C | 9.5 | 108 | 20°C |  | 12°C | 10.6 | 54 | 20°C |  | 12°C | 8.25 | 18
20°C |  | 18°C | 8.41 | 180 |  | 20°C |  | 18°C | 11 | 108 | 20°C |  | 18°C | 14 | 54 | 20°C |  | 18°C | 12.1 | 18
25°C |  | 7°C | 4.85 | 180 |  | 25°C |  | 7°C | 5.86 | 108 | 25°C |  | 7°C | 6.09 | 54 | 25°C |  | 7°C | 5.24 | 18
25°C |  | 12°C | 6.13 | 180 |  | 25°C |  | 12°C | 7.34 | 108 | 25°C |  | 12°C | 8.16 | 54 | 25°C |  | 12°C | 6.55 | 18
25°C |  | 18°C | 6.67 | 180 |  | 25°C |  | 18°C | 8.63 | 108 | 25°C |  | 18°C | 11.5 | 54 | 25°C |  | 18°C | 9.29 | 18
30°C |  | 7°C | 3.96 | 180 |  | 30°C |  | 7°C | 4.76 | 108 | 30°C |  | 7°C | 4.91 | 54 | 30°C |  | 7°C | 4.55 | 18
30°C |  | 12°C | 4.91 | 180 |  | 30°C |  | 12°C | 5.8 | 108 | 30°C |  | 12°C | 6.31 | 54 | 30°C |  | 12°C | 5.27 | 18
30°C |  | 18°C | 5.51 | 180 |  | 30°C |  | 18°C | 6.97 | 108 | 30°C |  | 18°C | 8.45 | 54 | 30°C |  | 18°C | 7.1 | 18
35°C |  | 7°C | 3.26 | 180 |  | 35°C |  | 7°C | 3.9 | 108 | 35°C |  | 7°C | 4 | 54 | 35°C |  | 7°C | 3.66 | 18
35°C |  | 12°C | 3.99 | 180 |  | 35°C |  | 12°C | 4.67 | 108 | 35°C |  | 12°C | 4.96 | 54 | 35°C |  | 12°C | 4.31 | 18
35°C |  | 18°C | 4.46 | 180 |  | 35°C |  | 18°C | 5.67 | 108 | 35°C |  | 18°C | 6.85 | 54 | 35°C |  | 18°C | 5.54 | 18
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% *Note2 | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 70 HP Pump 5.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.01 | 190 |  | -7°C | 60% | 35°C | 3.42 | 120 | -7°C | 30%*Note 2 | 35°C | 3.61 | 60 | -7°C | 10%*Note 3 | 35°C | 3.31 | 20
-7°C |  | 45°C | 2.59 | 185 |  | -7°C |  | 45°C | 2.86 | 120 | -7°C |  | 45°C | 2.93 | 60 | -7°C |  | 45°C | 2.68 | 20
-7°C |  | 55°C*Note 1 | 2.36 | 167 |  | -7°C |  | 55°C*Note 1 | 2.5 | 120 | -7°C |  | 55°C*Note 1 | 2.52 | 60 | -7°C |  | 55°C*Note 4 | 2.3 | 20
2°C |  | 35°C | 3.65 | 200 |  | 2°C |  | 35°C | 4.3 | 120 | 2°C |  | 35°C | 4.45 | 60 | 2°C |  | 35°C | 4.05 | 20
2°C |  | 45°C | 3.08 | 200 |  | 2°C |  | 45°C | 3.45 | 120 | 2°C |  | 45°C | 3.5 | 60 | 2°C |  | 45°C | 3.16 | 20
2°C |  | 55°C | 2.72 | 193 |  | 2°C |  | 55°C | 2.83 | 120 | 2°C |  | 55°C | 2.82 | 60 | 2°C |  | 55°C | 2.53 | 20
7°C |  | 35°C | 4.11 | 200 |  | 7°C |  | 35°C | 4.9 | 120 | 7°C |  | 35°C | 4.99 | 60 | 7°C |  | 35°C | 4.61 | 20
7°C |  | 45°C | 3.39 | 200 |  | 7°C |  | 45°C | 3.84 | 120 | 7°C |  | 45°C | 3.85 | 60 | 7°C |  | 45°C | 3.47 | 20
7°C |  | 55°C | 2.86 | 200 |  | 7°C |  | 55°C | 3.1 | 120 | 7°C |  | 55°C | 3.04 | 60 | 7°C |  | 55°C | 2.7 | 20
12°C |  | 35°C | 4.81 | 200 |  | 12°C |  | 35°C | 5.64 | 120 | 12°C |  | 35°C | 5.93 | 60 | 12°C |  | 35°C | 5.26 | 20
12°C |  | 45°C | 3.84 | 200 |  | 12°C |  | 45°C | 4.33 | 120 | 12°C |  | 45°C | 4.37 | 60 | 12°C |  | 45°C | 3.98 | 20
12°C |  | 55°C | 3.18 | 200 |  | 12°C |  | 55°C | 3.45 | 120 | 12°C |  | 55°C | 3.38 | 60 | 12°C |  | 55°C | 3.05 | 20
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 179L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 5.64 | 200 |  | 20°C | 60% | 7°C | 7.15 | 120 | 20°C | 30%*Note 1 | 7°C | 7.64 | 60 | 20°C | 10%*Note 2 | 7°C | 6.89 | 20
20°C |  | 12°C | 7.35 | 200 |  | 20°C |  | 12°C | 9.29 | 120 | 20°C |  | 12°C | 10.4 | 60 | 20°C |  | 12°C | 8.26 | 20
20°C |  | 18°C | 7.97 | 200 |  | 20°C |  | 18°C | 10.5 | 120 | 20°C |  | 18°C | 12.8 | 60 | 20°C |  | 18°C | 11.4 | 20
25°C |  | 7°C | 4.56 | 200 |  | 25°C |  | 7°C | 5.76 | 120 | 25°C |  | 7°C | 6.11 | 60 | 25°C |  | 7°C | 5.65 | 20
25°C |  | 12°C | 5.8 | 200 |  | 25°C |  | 12°C | 7.2 | 120 | 25°C |  | 12°C | 8.08 | 60 | 25°C |  | 12°C | 6.57 | 20
25°C |  | 18°C | 6.37 | 200 |  | 25°C |  | 18°C | 8.27 | 120 | 25°C |  | 18°C | 10.7 | 60 | 25°C |  | 18°C | 9.2 | 20
30°C |  | 7°C | 3.73 | 200 |  | 30°C |  | 7°C | 4.69 | 120 | 30°C |  | 7°C | 4.93 | 60 | 30°C |  | 7°C | 4.54 | 20
30°C |  | 12°C | 4.68 | 200 |  | 30°C |  | 12°C | 5.71 | 120 | 30°C |  | 12°C | 6.27 | 60 | 30°C |  | 12°C | 5.3 | 20
30°C |  | 18°C | 5.2 | 200 |  | 30°C |  | 18°C | 6.62 | 120 | 30°C |  | 18°C | 9.09 | 60 | 30°C |  | 18°C | 7.04 | 20
35°C |  | 7°C | 3.08 | 200 |  | 35°C |  | 7°C | 3.84 | 120 | 35°C |  | 7°C | 4.04 | 60 | 35°C |  | 7°C | 3.69 | 20
35°C |  | 12°C | 3.81 | 200 |  | 35°C |  | 12°C | 4.6 | 120 | 35°C |  | 12°C | 4.95 | 60 | 35°C |  | 12°C | 4.64 | 20
35°C |  | 18°C | 4.31 | 200 |  | 35°C |  | 18°C | 5.36 | 120 | 35°C |  | 18°C | 6.76 | 60 | 35°C |  | 18°C | 5.52 | 20
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 179L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 56.6/66.9/70.8 | 3.11 | 2.63 | 2.36 | 176 | 176 | 167
2°C | 54% | 24.7/30.9/37.9 | 4.37 | 3.49 | 2.85 | 108 | 108 | 108
7°C | 35% | 13.9/17.9/22.7 | 5.03 | 3.9 | 3.09 | 70 | 70 | 70
12°C | 12% *Note2 | 4.33/5.88/7.62 | 5.54 | 4.08 | 3.15 | 24 | 24 | 24
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 52.9/41.7/38.9 | 3.33 | 4.22 | 4.53 | 176 | 176 | 176
30°C | 54% | 22.5/18.3/15.4 | 4.79 | 5.91 | 7.02 | 108 | 108 | 108
25°C | 35% | 11.5/8.34/5.83 | 6.08 | 8.39 | 12 | 70 | 70 | 70
20°C | 12%*Note 1 | 3.46/2.76/2.29 | 6.94 | 8.71 | 10.5 | 24 | 24 | 24
*Note 1 - Values provided based on minimum flow rate conditions of 179L/Min

## 50 HP Pump 7.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.31 | 128 |  | -7°C | 60% | 35°C | 3.5 | 90 | -7°C | 30%*Note 2 | 35°C | 3.5 | 45 | -7°C | 10%*Note 3 | 35°C | 3.11 | 15
-7°C |  | 45°C | 2.79 | 126 |  | -7°C |  | 45°C | 2.89 | 90 | -7°C |  | 45°C | 2.81 | 45 | -7°C |  | 45°C | 2.5 | 15
-7°C |  | 55°C*Note 1 | 2.46 | 122 |  | -7°C |  | 55°C*Note 1 | 2.5 | 90 | -7°C |  | 55°C*Note 1 | 2.41 | 45 | -7°C |  | 55°C*Note 4 | 2.14 | 15
2°C |  | 35°C | 3.98 | 150 |  | 2°C |  | 35°C | 4.37 | 90 | 2°C |  | 35°C | 4.34 | 45 | 2°C |  | 35°C | 4 | 15
2°C |  | 45°C | 3.26 | 150 |  | 2°C |  | 45°C | 3.47 | 90 | 2°C |  | 45°C | 3.35 | 45 | 2°C |  | 45°C | 3.2 | 15
2°C |  | 55°C | 2.8 | 137 |  | 2°C |  | 55°C | 2.82 | 90 | 2°C |  | 55°C | 2.67 | 45 | 2°C |  | 55°C | 2.3 | 15
7°C |  | 35°C | 4.53 | 150 |  | 7°C |  | 35°C | 4.96 | 90 | 7°C |  | 35°C | 4.88 | 45 | 7°C |  | 35°C | 4.44 | 15
7°C |  | 45°C | 3.62 | 150 |  | 7°C |  | 45°C | 3.86 | 90 | 7°C |  | 45°C | 3.77 | 45 | 7°C |  | 45°C | 3.49 | 15
7°C |  | 55°C | 2.97 | 147 |  | 7°C |  | 55°C | 3.07 | 90 | 7°C |  | 55°C | 2.99 | 45 | 7°C |  | 55°C | 2.8 | 15
12°C |  | 35°C | 5.23 | 150 |  | 12°C |  | 35°C | 5.78 | 90 | 12°C |  | 35°C | 5.76 | 45 | 12°C |  | 35°C | 5.15 | 15
12°C |  | 45°C | 4.08 | 150 |  | 12°C |  | 45°C | 4.36 | 90 | 12°C |  | 45°C | 4.27 | 45 | 12°C |  | 45°C | 3.92 | 15
12°C |  | 55°C | 3.3 | 150 |  | 12°C |  | 55°C | 3.43 | 90 | 12°C |  | 55°C | 3.32 | 45 | 12°C |  | 55°C | 3.1 | 15
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.58 | 150 |  | 20°C | 60% | 7°C | 7.43 | 90 | 20°C | 30%*Note 1 | 7°C | 7.62 | 45 | 20°C | 10%*Note 2 | 7°C | 6.33 | 15
20°C |  | 12°C | 8.5 | 150 |  | 20°C |  | 12°C | 9.86 | 90 | 20°C |  | 12°C | 10 | 45 | 20°C |  | 12°C | 8.24 | 15
20°C |  | 18°C | 9.2 | 150 |  | 20°C |  | 18°C | 12 | 90 | 20°C |  | 18°C | 11.5 | 45 | 20°C |  | 18°C | 12.1 | 15
25°C |  | 7°C | 5.3 | 150 |  | 25°C |  | 7°C | 5.97 | 90 | 25°C |  | 7°C | 6.12 | 45 | 25°C |  | 7°C | 5.18 | 15
25°C |  | 12°C | 6.63 | 150 |  | 25°C |  | 12°C | 7.57 | 90 | 25°C |  | 12°C | 7.77 | 45 | 25°C |  | 12°C | 6.57 | 15
25°C |  | 18°C | 7.15 | 150 |  | 25°C |  | 18°C | 9.68 | 90 | 25°C |  | 18°C | 9.4 | 45 | 25°C |  | 18°C | 9.49 | 15
30°C |  | 7°C | 4.3 | 150 |  | 30°C |  | 7°C | 4.86 | 90 | 30°C |  | 7°C | 4.9 | 45 | 30°C |  | 7°C | 4.29 | 15
30°C |  | 12°C | 5.28 | 150 |  | 30°C |  | 12°C | 5.96 | 90 | 30°C |  | 12°C | 6.47 | 45 | 30°C |  | 12°C | 5.27 | 15
30°C |  | 18°C | 5.75 | 150 |  | 30°C |  | 18°C | 7.76 | 90 | 30°C |  | 18°C | 8.75 | 45 | 30°C |  | 18°C | 7.26 | 15
35°C |  | 7°C | 3.53 | 150 |  | 35°C |  | 7°C | 3.99 | 90 | 35°C |  | 7°C | 3.96 | 45 | 35°C |  | 7°C | 3.58 | 15
35°C |  | 12°C | 4.27 | 150 |  | 35°C |  | 12°C | 4.78 | 90 | 35°C |  | 12°C | 4.99 | 45 | 35°C |  | 12°C | 4.29 | 15
35°C |  | 18°C | 4.7 | 150 |  | 35°C |  | 18°C | 6.16 | 90 | 35°C |  | 18°C | 6.55 | 45 | 35°C |  | 18°C | 5.62 | 15
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | COP 35℃ | COP 45℃ | COP 55°C | LWT 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 38.7/ 45.3/ 49.6 | 3.31 | 2.79 | 2.46 | 128 | 126 | 122
2°C | 54% | 18.4/ 23.2/ 28.7 | 4.4 | 3.49 | 2.82 | 81 | 81 | 81
7°C | 35% | 12/ 10.6/ 14 | 4.93 | 3.76 | 2.97 | 52.5 | 52.5 | 52.5
12°C | 12% *Note2 | 3.45/ 4.51/ 5.7 | 5.22 | 3.99 | 3.16 | 18 | 18 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) 35/45/55 | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 35.8/ 28.6/ 26.9 | 3.69 | 4.61 | 4.9 | 132 | 132 | 132
30°C | 54% | 16.6/ 12.8/ 9.62 | 4.89 | 6.35 | 8.42 | 81 | 81 | 81
25°C | 35% | 8.58/ 5.93/ 4.53 | 6.12 | 8.85 | 11.6 | 52.5 | 52.5 | 52.5
20°C | 12%*Note 1 | 2.82/ 2.06/ 1.48 | 6.39 | 8.75 | 12.2 | 18 | 18 | 18
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 60 HP Pump 7.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.21 | 150 |  | -7°C | 60% | 35°C | 3.45 | 108 | -7°C | 30% | 35°C | 3.64 | 54 | -7°C | 10%*Note 2 | 35°C | 3.3 | 18
-7°C |  | 45°C | 2.72 | 149 |  | -7°C |  | 45°C | 2.87 | 108 | -7°C |  | 45°C | 2.94 | 54 | -7°C |  | 45°C | 2.66 | 18
-7°C |  | 55°C*Note 1 | 2.42 | 141 |  | -7°C |  | 55°C*Note 1 | 2.5 | 108 | -7°C |  | 55°C*Note 1 | 2.52 | 54 | -7°C |  | 55°C*Note 3 | 2.28 | 18
2°C |  | 35°C | 3.77 | 180 |  | 2°C |  | 35°C | 4.33 | 108 | 2°C |  | 35°C | 4.48 | 54 | 2°C |  | 35°C | 4.04 | 18
2°C |  | 45°C | 3.15 | 180 |  | 2°C |  | 45°C | 3.46 | 108 | 2°C |  | 45°C | 3.52 | 54 | 2°C |  | 45°C | 3.13 | 18
2°C |  | 55°C | 2.73 | 157 |  | 2°C |  | 55°C | 2.83 | 108 | 2°C |  | 55°C | 2.82 | 54 | 2°C |  | 55°C | 2.49 | 18
7°C |  | 35°C | 4.26 | 180 |  | 7°C |  | 35°C | 4.96 | 108 | 7°C |  | 35°C | 5.03 | 54 | 7°C |  | 35°C | 4.63 | 18
7°C |  | 45°C | 3.47 | 180 |  | 7°C |  | 45°C | 3.88 | 108 | 7°C |  | 45°C | 3.86 | 54 | 7°C |  | 45°C | 3.44 | 18
7°C |  | 55°C | 2.94 | 169 |  | 7°C |  | 55°C | 3.1 | 108 | 7°C |  | 55°C | 3.04 | 54 | 7°C |  | 55°C | 2.65 | 18
12°C |  | 35°C | 4.96 | 180 |  | 12°C |  | 35°C | 5.76 | 108 | 12°C |  | 35°C | 5.93 | 54 | 12°C |  | 35°C | 5.32 | 18
12°C |  | 45°C | 3.92 | 180 |  | 12°C |  | 45°C | 4.4 | 108 | 12°C |  | 45°C | 4.44 | 54 | 12°C |  | 45°C | 4.07 | 18
12°C |  | 55°C | 3.22 | 180 |  | 12°C |  | 55°C | 3.48 | 108 | 12°C |  | 55°C | 3.47 | 54 | 12°C |  | 55°C | 3.23 | 18
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
*Note 3 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 6.02 |  |  | 20°C | 60% | 7°C | 7.26 |  | 20°C | 30% | 7°C | 7.64 |  | 20°C | 10%*Note 1 | 7°C | 6.39
20°C |  | 12°C | 7.79 |  |  | 20°C |  | 12°C | 9.5 |  | 20°C |  | 12°C | 10.6 |  | 20°C |  | 12°C | 8.25
20°C |  | 18°C | 8.41 |  |  | 20°C |  | 18°C | 11 |  | 20°C |  | 18°C | 14 |  | 20°C |  | 18°C | 12.1
25°C |  | 7°C | 4.85 |  |  | 25°C |  | 7°C | 5.86 |  | 25°C |  | 7°C | 6.09 |  | 25°C |  | 7°C | 5.24
25°C |  | 12°C | 6.13 |  |  | 25°C |  | 12°C | 7.34 |  | 25°C |  | 12°C | 8.16 |  | 25°C |  | 12°C | 6.55
25°C |  | 18°C | 6.67 |  |  | 25°C |  | 18°C | 8.63 |  | 25°C |  | 18°C | 11.5 |  | 25°C |  | 18°C | 9.29
30°C |  | 7°C | 4.85 |  |  | 30°C |  | 7°C | 4.76 |  | 30°C |  | 7°C | 4.91 |  | 30°C |  | 7°C | 4.55
30°C |  | 12°C | 6.13 |  |  | 30°C |  | 12°C | 5.8 |  | 30°C |  | 12°C | 6.31 |  | 30°C |  | 12°C | 5.27
30°C |  | 18°C | 6.67 |  |  | 30°C |  | 18°C | 6.97 |  | 30°C |  | 18°C | 8.45 |  | 30°C |  | 18°C | 7.1
35°C |  | 7°C | 3.96 |  |  | 35°C |  | 7°C | 3.9 |  | 35°C |  | 7°C | 4 |  | 35°C |  | 7°C | 3.66
35°C |  | 12°C | 4.91 |  |  | 35°C |  | 12°C | 4.67 |  | 35°C |  | 12°C | 4.96 |  | 35°C |  | 12°C | 4.31
35°C |  | 18°C | 5.41 |  |  | 35°C |  | 18°C | 5.67 |  | 35°C |  | 18°C | 6.85 |  | 35°C |  | 18°C | 5.54
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note 1
-7°C | 88% | 42.7/5.7/57.6 | 3.28 | 2.76 | 2.43 | 140 | 140 | 140
2°C | 54% | 22/27.7/33.36 | 4.42 | 3.51 | 2.89 | 97.2 | 97.2 | 97.2
7°C | 35% | 12.4/16/20.3 | 5.09 | 3.93 | 3.11 | 63 | 63 | 63
12°C | 12% *Note2 | 3.88/5.31/6.9 | 5.56 | 4.07 | 3.13 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 38.5/31.2/29.1 | 3.65 | 4.5 | 4.82 | 140 | 140 | 140
30°C | 54% | 20.1/15.8/13.1 | 4.83 | 6.17 | 7.39 | 97.2 | 97.2 | 97.2
25°C | 35% | 10.4/7.41/5.12 | 6.07 | 8.5 | 12.3 | 63 | 63 | 63
20°C | 12%*Note 1 | 3.12/2.47/1.98 | 6.92 | 8.73 | 10.9 | 21.6 | 21.6 | 21.6
*Note 1 - Values provided based on minimum flow rate conditions of 150L/Min

## 70 HP Pump 7.5 kW
1. Heating Performance Table (COP)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | COP | Power output [kW]
-7°C | 100% | 35°C | 3.01 | 190 |  | -7°C | 60% | 35°C | 3.42 | 120 | -7°C | 30%*Note 2 | 35°C | 3.61 | 60 | -7°C | 10%*Note 3 | 35°C | 3.31 | 20
-7°C |  | 45°C | 2.59 | 185 |  | -7°C |  | 45°C | 2.86 | 120 | -7°C |  | 45°C | 2.93 | 60 | -7°C |  | 45°C | 2.68 | 20
-7°C |  | 55°C*Note 1 | 2.36 | 167 |  | -7°C |  | 55°C*Note 1 | 2.5 | 120 | -7°C |  | 55°C*Note 1 | 2.52 | 60 | -7°C |  | 55°C*Note 4 | 2.3 | 20
2°C |  | 35°C | 3.65 | 200 |  | 2°C |  | 35°C | 4.3 | 120 | 2°C |  | 35°C | 4.45 | 60 | 2°C |  | 35°C | 4.05 | 20
2°C |  | 45°C | 3.08 | 200 |  | 2°C |  | 45°C | 3.45 | 120 | 2°C |  | 45°C | 3.5 | 60 | 2°C |  | 45°C | 3.16 | 20
2°C |  | 55°C | 2.66 | 187 |  | 2°C |  | 55°C | 2.83 | 120 | 2°C |  | 55°C | 2.82 | 60 | 2°C |  | 55°C | 2.53 | 20
7°C |  | 35°C | 4.11 | 200 |  | 7°C |  | 35°C | 4.9 | 120 | 7°C |  | 35°C | 4.99 | 60 | 7°C |  | 35°C | 4.61 | 20
7°C |  | 45°C | 3.39 | 200 |  | 7°C |  | 45°C | 3.84 | 120 | 7°C |  | 45°C | 3.85 | 60 | 7°C |  | 45°C | 3.47 | 20
7°C |  | 55°C | 2.86 | 200 |  | 7°C |  | 55°C | 3.1 | 120 | 7°C |  | 55°C | 3.04 | 60 | 7°C |  | 55°C | 2.7 | 20
12°C |  | 35°C | 4.81 | 200 |  | 12°C |  | 35°C | 5.64 | 120 | 12°C |  | 35°C | 5.93 | 60 | 12°C |  | 35°C | 5.26 | 20
12°C |  | 45°C | 3.84 | 200 |  | 12°C |  | 45°C | 4.33 | 120 | 12°C |  | 45°C | 4.37 | 60 | 12°C |  | 45°C | 3.98 | 20
12°C |  | 55°C | 3.18 | 200 |  | 12°C |  | 55°C | 3.45 | 120 | 12°C |  | 55°C | 3.38 | 60 | 12°C |  | 55°C | 3.05 | 20
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided under delta T of 4.3°C
*Note 3 - Values provided based on minimum flow rate conditions of 179L/Min
*Note 4 - Max LWT = 53°C
2. Table of Cooling Performance (EER)
This table should show the COP (Coefficient of Performance) of the heat pump at different outside temperatures and flow temperatures. *Where possible, temperature difference of 5K performed when carrying out calculations *Relative humidity of 86.646% used for all calculations
Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] |  | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW] | Outside temperature (°C) | Load factor | Flow temperature (°C) | EER | Power output [kW]
20°C | 100% | 7°C | 5.64 | 200 |  | 20°C | 60% | 7°C | 7.15 | 120 | 20°C | 30%*Note 1 | 7°C | 7.64 | 60 | 20°C | 10%*Note 2 | 7°C | 6.88 | 20
20°C |  | 12°C | 7.35 | 200 |  | 20°C |  | 12°C | 9.29 | 120 | 20°C |  | 12°C | 10.4 | 60 | 20°C |  | 12°C | 8.26 | 20
20°C |  | 18°C | 7.97 | 200 |  | 20°C |  | 18°C | 10.5 | 120 | 20°C |  | 18°C | 12.8 | 60 | 20°C |  | 18°C | 11.4 | 20
25°C |  | 7°C | 4.56 | 200 |  | 25°C |  | 7°C | 5.76 | 120 | 25°C |  | 7°C | 6.11 | 60 | 25°C |  | 7°C | 5.64 | 20
25°C |  | 12°C | 5.8 | 200 |  | 25°C |  | 12°C | 7.2 | 120 | 25°C |  | 12°C | 8.08 | 60 | 25°C |  | 12°C | 6.57 | 20
25°C |  | 18°C | 6.37 | 200 |  | 25°C |  | 18°C | 8.27 | 120 | 25°C |  | 18°C | 10.7 | 60 | 25°C |  | 18°C | 9.19 | 20
30°C |  | 7°C | 3.73 | 200 |  | 30°C |  | 7°C | 4.69 | 120 | 30°C |  | 7°C | 4.93 | 60 | 30°C |  | 7°C | 4.54 | 20
30°C |  | 12°C | 4.68 | 200 |  | 30°C |  | 12°C | 5.71 | 120 | 30°C |  | 12°C | 6.27 | 60 | 30°C |  | 12°C | 5.3 | 20
30°C |  | 18°C | 5.2 | 200 |  | 30°C |  | 18°C | 6.62 | 120 | 30°C |  | 18°C | 9.09 | 60 | 30°C |  | 18°C | 7.03 | 20
35°C |  | 7°C | 3.08 | 200 |  | 35°C |  | 7°C | 3.84 | 120 | 35°C |  | 7°C | 4.04 | 60 | 35°C |  | 7°C | 3.68 | 20
35°C |  | 12°C | 3.81 | 200 |  | 35°C |  | 12°C | 4.6 | 120 | 35°C |  | 12°C | 4.95 | 60 | 35°C |  | 12°C | 4.63 | 20
35°C |  | 18°C | 4.31 | 200 |  | 35°C |  | 18°C | 5.36 | 120 | 35°C |  | 18°C | 6.76 | 60 | 35°C |  | 18°C | 5.52 | 20
*Note 1 - Values provided under delta T of 4.3°C
*Note 2 - Values provided based on minimum flow rate conditions of 179L/Min
3. Table of Partial Loads
Tables for Heating Mode
These tables show the heat output (in kW) and the COP (Coefficient of Performance) at different outdoor temperatures and at different flow temperatures, for various load percentages. The load conditions are labelled with the letters A, B, C, D, which correspond to specific load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | COP 35℃ | COP 45℃ | COP 55°C | T Delivery 35°C (kW) | LWT 45℃ | LWT 55℃ *Note1
-7°C | 88% | 56.6/66.9/70.8 | 3.11 | 2.63 | 2.36 | 176 | 176 | 167
2°C | 54% | 24.7/30.9/37.9 | 4.37 | 3.49 | 2.85 | 108 | 108 | 108
7°C | 35% | 13.9/17.9/22.7 | 5.03 | 3.9 | 3.09 | 70 | 70 | 70
12°C | 12% *Note2 | 4.33/5.88/7.62 | 5.54 | 4.08 | 3.15 | 24 | 24 | 24
*Note 1 - Values provided under conditions 53°C / 48°C
*Note 2 - Values provided based on minimum flow rate conditions of 150L/Min
Tables for Cooling Mode
These tables show the heat output (in kW) and COP (in cooling mode, indicated as EER) at different outdoor temperatures and at different flow temperatures, again for the various load percentages: 88%, 54%, 35%, and 12%.
Source temperature (°C) | Load Factor (%) | Thermal Power Output (kW) | EER 7℃ | EER 13°C | EER 18°C | LWT7°C (kW) | LWT 13℃ | LWT 18℃
35°C | 88% | 52.9/41.7/38.9 | 3.33 | 4.22 | 4.53 | 176 | 176 | 176
30°C | 54% | 22.5/18.3/15.4 | 4.79 | 5.91 | 7.02 | 108 | 108 | 108
25°C | 35% | 11.5/8.34/5.83 | 6.08 | 8.39 | 12 | 70 | 70 | 70
20°C | 12%*Note 1 | 3.46/2.76/2.29 | 6.94 | 8.71 | 10.5 | 24 | 24 | 24
*Note 1 - Values provided based on minimum flow rate conditions of 179L/Min